## Allgemeine_Konst. (hidden)
Allgemeine Konstante
Netzteil
Imax | 3.5
Ubmin | 19.2
Ubmax | 32
Pmax | 60
PAlarm | 54
PmaxIO | 58
TUmin | 40
Gleichtzeitigkeitsfaktor 1 MT24 | 100
Gleichtzeitigkeitsfaktor 2 MT24 | 100
Gleichtzeitigkeitsfaktor 3 MT24 | 100
Gleichtzeitigkeitsfaktor 1 MT16 | 100
Gleichtzeitigkeitsfaktor 2 MT16 | 100
Gleichtzeitigkeitsfaktor 3 MT16 | 100
Gleichtzeitigkeitsfaktor 1 MT08 | 100
Gleichtzeitigkeitsfaktor 2 MT08 | 100
Gleichtzeitigkeitsfaktor 3 MT08 | 100

## Netzteile (hidden)
Netzteil und Konstante
| Pmax | P0 | Pch
BM1 | 0 | 0 | 0
PSM24-3G.1 | 0 | 0 | 0

## Gateways (hidden)
Gateway und Konstante
| Pmax | P0 | Pch
BM1 | 0 | 0 | 0
GDP-NI | 1 | 1 | 0
GDP-IS | 1 | 1 | 0
GEN-3G | 1.5 | 1.5 | 0

## Module (hidden)
Modue und Konstanste
| Pmax | P0 | Parbeit | lfnr. | lfnr. V1.2 | lfnr. V1.4
BM1 | 0 | 0 | 0 | 1 | 1 | 1
AI41EX | 2 | 2 | 0 | 2 | 2 | 2
AI401EX | 2.2 | 2.2 | 0 | 3 | 3 | 3
AI43EX | 1.5 | 1.5 | 0 | 4 | 4 | 4
AIH401EX | 3 | 1.5 | 0 |  | 5 | 5
AIH40EX | 3 | 3 | 0 | 5 | 6 | 6
AIH41EX | 1.5 | 1.5 | 0 | 6 | 7 | 7
AO401EX | 2.5 | 2.5 | 0 | 7 | 8 | 8
AOH401EX | 3 | 1.5 | 0 |  | 9 | 9
AOH40EX | 3 | 3 | 0 | 8 | 10 | 10
DF20EX | 1 | 1 | 0 | 9 | 11 | 11
DI401EX | 2 | 2 | 0 | 10 | 12 | 12
DM80EX | 1 | 1 | 0 | 11 | 13 | 13
DO401EX | 4.5 | 0.9 | 3.6 | 12 | 14 | 14
TI40EX | 1 | 1 | 0 | 13 | 15 | 15
TI401EX | 1 | 0.5 | 0 |  |  | 17
TI41EX | 1 | 1 | 0 | 14 | 16 | 16
Achtung: Modulerweiterungen in dieser Liste haben ggf. Auswirkungen auf die Auswahl ob die 60er Kennlinien oder 70er Kennlinien zu nutzen sind, da die Zahlennummer der Module zur Auswertung kommt.

## Variable (hidden)
Variable
Variable | Wert | Resultat
Sprache | 2 | Ausgewählte Sprache ist: English
Installationsort MT24 | 3
Installationsort MT16 | 3
Installationsort MT08 | 2
Gleichzeitigkeitsfaktor MT24 | 100
Gleichzeitigkeitsfaktor MT16 | 100
Gleichzeitigkeitsfaktor MT08 | 100
Gateway
Temperaturklasse MT24-3G | 2
Temperaturklasse MT16-3G | 2
Temperaturklasse MT08-3G | 2

## Sprache (hidden)
Deutsch | Language
English
Sprache | Language
Bearbeiter: | Reviser:
Projekt: | Project:
Racknummer: | Rack number:
Datum: | Data:
Installation: | Installation:
Installation im Schaltraum | Installation in Control room
Gehäuse 800mm x 550mm x 260mm | Housing 800mm x 550mm x 260 mm
Gehäuse 650mm x 550mm x 260mm | Housing 650mm x 550mm x 260 mm
Gehäuse 460mm x 550mm x 260mm | Housing 460mm x 550mm x 260 mm
AC Vorschaltnetzteil | AC pre power Supply
Minimale Eingangsspannung: | Minimal input voltage:
Gleichzeitigskeitfaktor: | Synchronous load:
Gleichzeitigskeitfaktor n.a. | Synchronous load n.a.
Gesamtverlustleistung excom Module: | Total power consumption excom I/O modules:
Gesamtverlustleistung: | Total power consumption:
ACHTUNG: Verlustleistung I/O-Module überschritten! | ATTENTION: Power consumption I/O modules exceeded!
ACHTUNG: Leistungsreserve für I/O-Module | ATTENTION: Power reserve for I/O modules
ACHTUNG: Maximale Umgebungstemperatur < 40 °C! | ATTENTION: Maximum ambient temperature < 40 °C!
ACHTUNG: 3G-Installation erfordert GDP-IS! | ATTENTION: 3G installation requires GDP-IS!
ACHTUNG: Schaltschrankinstallation erfordert GDP-NI! | ATTENTION: Controll room installation requires GDP-NI!
Maximale Umgebungstemperatur: | Maximum ambient temperature:
Bei Schaltraumontage kann im nicht Ex-Bereich das Gateway GDP-NI verwendet werden. In diesem Fall ist ein separater Segmentkoppler nicht erforderlich. | By installing the system in a control room in the save area the gateway GDP-NI can be used. This case do not required a separate segment coupler.
Bei Schaltschrankmontage im Ex-Bereich ist das Gateway GDP-IS zu verwenden. In diesem Fall ist ein zusätzlicher Segmentkoppler erforderlich. | By installing the system in a cabinet in the hazardous area the gateway GDP-IS has to be used. This case required a segment coupler.
Steckplatz | Slot
Typ | Type
Leistung | Power
Spannungsversorgung 1 | Power supply 1
Spannungsversorgung 2 | Power supply 2
Spannungsversorgung | Power supply
Gateway 1 | Gateway 1
Gateway 2 | Gateway 2
Gateway | Gateway
Steckplatz 1 | Slot 1
Steckplatz 2 | Slot 2
Steckplatz 3 | Slot 3
Steckplatz 4 | Slot 4
Steckplatz 5 | Slot 5
Steckplatz 6 | Slot 6
Steckplatz 7 | Slot 7
Steckplatz 8 | Slot 8
Steckplatz 9 | Slot 9
Steckplatz 10 | Slot 10
Steckplatz 11 | Slot 11
Steckplatz 12 | Slot 12
Steckplatz 13 | Slot 13
Steckplatz 14 | Slot 14
Steckplatz 15 | Slot 15
Steckplatz 16 | Slot 16
Steckplatz 17 | Slot 17
Steckplatz 18 | Slot 18
Steckplatz 19 | Slot 19
Steckplatz 20 | Slot 20
Steckplatz 21 | Slot 21
Steckplatz 22 | Slot 22
Steckplatz 23 | Slot 23
Steckplatz 24 | Slot 24
Zusätzlich Verlustleistung | Additional power consumption
Temperaturklasse | Temperature Class
Diese Auswahl erlaubt nicht die Benutzung folgender Module: AI41EX, AIH40EX, AIH41EX, AOH40EX, TI40EX | This selection does not allow the use of the following modules: AI41EX, AIH40EX, AIH41EX, AOH40EX, TI40EX

## Gehaeuse60 (hidden)
| Installation |  |  | Umgebungstemperatur für
| Ort | Tu | Pges | 60 | 55 | 50 | 45 | 40 | 35 | 30
MT24-3G | Installation in Control room | 60 | 0 | 60 | 60 | 60 | 60 | 60
| Housing 800mm x 550mm x 260 mm | 60 | 0 |  | 6 | 28 | 46 | 58
| Housing 650mm x 550mm x 260 mm | 60 | 0 |  | 6 | 22 | 38 | 55
| Housing 460mm x 550mm x 260 mm | 60 | 0 |  | 7 | 19 | 32 | 36
MT16-3G | Installation in Control room | 60 | 0 | 60 | 60 | 60 | 60 | 60
| Housing 800mm x 550mm x 260 mm | 60 | 0 |  | 6 | 28 | 46 | 58
| Housing 650mm x 550mm x 260 mm | 60 | 0 |  | 6 | 22 | 38 | 55
| Housing 460mm x 550mm x 260 mm | 60 | 0 |  | 7 | 19 | 32 | 36
08-3G | Installation in Control room | 60 | 0 | 60 | 60 | 60 | 60 | 60
| Housing 460mm x 550mm x 260 mm | 60 | 0 |  | 7 | 19 | 32 | 36

## Gehaeuse70 (hidden)
| Installation |  |  | Umgebungstemperatur für
| Ort | Tu | Pges | 65 °C | 60 °C | 55 °C | 50 °C | 45 °C | 40 °C | 35 °C | 30 °C
MT24-3G | Installation in Control room | 70 | 0 | 70 | 70 | 70 | 70 | 70 | 70
| Housing 800mm x 550mm x 260 mm | 65 °C | 0 | 6 | 28 | 46 | 58 | 58 | 58
| Housing 650mm x 550mm x 260 mm | 65 °C | 0 | 6 | 22 | 39 | 55 | 58 | 58
| Housing 460mm x 550mm x 260 mm | 65 °C | 0 | 7 | 19 | 32 | 36 | 36 | 36
MT16-3G | Installation in Control room | 70 | 0 | 70 | 70 | 70 | 70 | 70 | 70
| Housing 800mm x 550mm x 260 mm | 65 °C | 0 | 6 | 28 | 46 | 58 | 58 | 58
| Housing 650mm x 550mm x 260 mm | 65 °C | 0 | 6 | 22 | 39 | 55 | 58 | 58
| Housing 460mm x 550mm x 260 mm | 65 °C | 0 | 7 | 19 | 32 | 36 | 36 | 36
08-3G | Installation in Control room | 70 | 0 | 70 W | 70 W | 70 W | 70 W | 70 W | 70 W
| Housing 460mm x 550mm x 260 mm | 65 °C | 0 | 7 | 19 | 32 | 36 | 36 | 36

## Introduction
Input for project information possible
Possible housing variants
Choice of temperature class of modules. At 70 ° C, the modules listed below may not be used. If this happens nevertheless, the 60 °C characteristic is used automatically.
Maximum power consumption per module
Total power loss considering 90% efficiency
Printout by predefined area
Choice of modules to use
Remark: Do not use different gateways together in a rack!
Simultaneity factor for all DO401... channels on the module rack.
Example: 2 x DO401 installed. If max. 4 of the 8 outputs are active at the same time, the simultaneity factor is 0.5.

## MT24-3G
[10 empty] | Reviser: |  |  |  | Max Mustermann
Reviser: | Max Mustermann | [8 empty] | Project: |  |  |  | Configuration MT24-3G V1.5.0
Project: | Configuration MT24-3G V1.5.0 | [8 empty] | Rack number: |  |  |  | -
Rack number: | - | [8 empty] | Data: |  |  |  | 2025-03-26
Data: | 2025-03-26
Slot |  | Type | Power
Power supply 1 |  | 2 | 0 |  |  |  | 1 | PSM24-3G.1 | BM1 | BM1 | BM1 | BM1 | BM1 | BM1 | BM1 | BM1 | BM1 | BM1 | BM1 | BM1 | BM1 | BM1 | BM1 | BM1 | BM1 | BM1 | BM1 | BM1 | BM1 | BM1 | BM1 | BM1 | BM1 | BM1 | BM1
Power supply 2 |  | 1 | 0
Gateway 1 |  | 1 | 0
Gateway 2 |  | 1 | 0 |  |  | This selection does not allow the use of the following modules: AI41EX, AIH40EX, AIH41EX, AOH40EX, TI40EX
Slot 1 |  | 1 | 0
Slot 2 |  | 1 | 0
Slot 3 |  | 1 | 0 | By installing the system in a cabinet in the hazardous area the gateway GDP-IS has to be used. This case required a segment coupler.
Slot 4 |  | 1 | 0
Slot 5 |  | 1 | 0
Slot 6 |  | 1 | 0
Slot 7 |  | 1 | 0
Slot 8 |  | 1 | 0
Slot 9 |  | 1 | 0
Slot 10 |  | 1 | 0 | Total power consumption excom I/O modules: | 0
Slot 11 |  | 1 | 0 | Total power consumption: | 0 |  |  | Housing 650mm x 550mm x 260 mm
Slot 12 |  | 1 | 0 | Maximum ambient temperature: | 65 °C |  |  | By installing the system in a cabinet in the hazardous area the gateway GDP-IS has to be used. This case required a segment coupler.
Slot 13 |  | 1 | 0 | [17 empty] | Total power consumption excom I/O modules: | [10 empty] | 0
Slot 14 |  | 1 | 0 | [17 empty] | Total power consumption: | [10 empty] | 0
Slot 15 |  | 1 | 0 | [17 empty] | Maximum ambient temperature: | [10 empty] | 65 °C
Slot 16 |  | 1 | 0
Slot 17 |  | 1 | 0
Slot 18 |  | 1 | 0
Slot 19 |  | 1 | 0
Slot 20 |  | 1 | 0
Slot 21 |  | 1 | 0
Slot 22 |  | 1 | 0
Slot 23 |  | 1 | 0
Slot 24 |  | 1 | 0
Control room
Installationsort
Housing 800 mm x 550 mm x 260 mm
Housing 650 mm x 550 mm x 260 mm
Temperature Class
60 °C
70 °C
Simultaneity factor

## MT16-3G
Reviser: | Max Mustermann
Project: | Configuration MT16-3G V1.5.0
Rack number: | -
Data: | 2025-03-26
Slot |  | Type | Power
Power supply 1 |  | 2 | 0 |  |  |  | 1 | PSM24-3G.1 | BM1 | BM1 | BM1 | BM1 | BM1 | BM1 | BM1 | BM1 | BM1 | BM1 | BM1 | BM1 | BM1 | BM1 | BM1 | BM1 | BM1 | BM1 | BM1
Power supply 2 |  | 1 | 0
Gateway 1 |  | 1 | 0
Gateway 2 |  | 1 | 0 |  |  | This selection does not allow the use of the following modules: AI41EX, AIH40EX, AIH41EX, AOH40EX, TI40EX
Slot 1 |  | 1 | 0
Slot 2 |  | 1 | 0
Slot 3 |  | 1 | 0 | By installing the system in a cabinet in the hazardous area the gateway GDP-IS has to be used. This case required a segment coupler.
Slot 4 |  | 1 | 0
Slot 5 |  | 1 | 0
Slot 6 |  | 1 | 0
Slot 7 |  | 1 | 0
Slot 8 |  | 1 | 0
Slot 9 |  | 1 | 0
Slot 10 |  | 1 | 0 | Total power consumption excom I/O modules: | 0
Slot 11 |  | 1 | 0 | Total power consumption: | 0
Slot 12 |  | 1 | 0 | Maximum ambient temperature: | 65 °C
Slot 13 |  | 1 | 0
Slot 14 |  | 1 | 0 |  |  |  |  | Reviser: |  |  |  | Max Mustermann
Slot 15 |  | 1 | 0 |  |  |  |  | Project: |  |  |  | Configuration MT16-3G V1.5.0
Slot 16 |  | 1 | 0 |  |  |  |  | Rack number: |  |  |  | -
[8 empty] | Data: |  |  |  | 2025-03-26
Housing 650mm x 550mm x 260 mm
By installing the system in a cabinet in the hazardous area the gateway GDP-IS has to be used. This case required a segment coupler.
[8 empty] | Total power consumption excom I/O modules: | [10 empty] | 0
[8 empty] | Total power consumption: | [10 empty] | 0
[8 empty] | Maximum ambient temperature: | [10 empty] | 65 °C
Installationsort
Control room
Housing 800 mm x 550 mm x 260 mm
Housing 650 mm x 550 mm x 260 mm
Temperature Class
60 °C
70 °C
Simultaneity factor

## MT08-3G
Reviser: | Max Mustermann
Project: | Configuration MT08-3G V1.5.0
Rack number: | -
Data: | 2025-03-26
Slot |  | Type | Power
Power supply 1 |  | 2 | 0 |  |  |  | 1 | PSM24-3G.1 | BM1 | BM1 | BM1 | BM1 | BM1 | BM1 | BM1 | BM1 | BM1 | BM1 | BM1
Power supply 2 |  | 1 | 0
Gateway 1 |  | 1 | 0
Gateway 2 |  | 1 | 0 |  |  | This selection does not allow the use of the following modules: AI41EX, AIH40EX, AIH41EX, AOH40EX, TI40EX
Slot 1 |  | 1 | 0
Slot 2 |  | 1 | 0
Slot 3 |  | 1 | 0 | By installing the system in a cabinet in the hazardous area the gateway GDP-IS has to be used. This case required a segment coupler.
Slot 4 |  | 1 | 0
Slot 5 |  | 1 | 0
Slot 6 |  | 1 | 0 | Total power consumption excom I/O modules: | 0
Slot 7 |  | 1 | 0 | Total power consumption: | 0
Slot 8 |  | 1 | 0 | Maximum ambient temperature: | 65 °C
[8 empty] | Reviser: |  |  |  | Max Mustermann
[8 empty] | Project: |  |  |  | Configuration MT08-3G V1.5.0
[8 empty] | Rack number: |  |  |  | -
[8 empty] | Data: |  |  |  | 2025-03-26
Housing 460mm x 550mm x 260 mm
By installing the system in a cabinet in the hazardous area the gateway GDP-IS has to be used. This case required a segment coupler.
[8 empty] | Total power consumption excom I/O modules: | [10 empty] | 0
[8 empty] | Total power consumption: | [10 empty] | 0
[8 empty] | Maximum ambient temperature: | [10 empty] | 65 °C
Control Room
Installationsort
Housing 460 mm x 550 mm x 260 mm
Temperature Class
60 °C
70 °C
Simultaneity factor

## Historie (hidden)
Version | Datum | Änderung | Fehler | Festgestellt | behoben
1.1 | 2018-07-31 | 1te Freigabe
1.2 d1 | 2018-11-20 | Übernahme der Zone 1 Kennlinie auf Basis neuer der Herstellererklärung
| 2018-11-20 | AIH401EX hinzugefügt Reihenfolge
| 2018-11-20 | AOH401EX hinzugefügt Reighenfolge
| 2018-11-14 | Hormonisierung der Sprachen
1.2 d2 | 2019-01-03 | Projektname auf englisch umgestellt | Projektname auf deutsch | 2018-12-10 | 2019-01-03
| 2019-01-04 | Hinweis für Sicheren Bereich auf can be used geändert |  | 2018-12-10 | 2019-01-04
|  | MT24-3G 65er Gegäuse gelöscht da derzeit die Kennlinie nicht vorhanden ist. | Für den MT24-3G haben wir keine separate Temperaturbetrachtung im 65er Gehäuse | 2018-12-10
|  |  | Nur Leistungsbetrachtung der I/O Module in Tabelle berücksichtigen (58W maximal) | 2019-01-04
| 2019-01-04 | Zeilen fur die Eingabe der zusätzlichen Verlustleistung gelöscht und Felder gesperrt | Keine Zusätzliche Verlustleistung möglich | 2018-12-10 | 2019-01-04
| 2019-01-04 | Bereiche gesperrt | Bereiche Können trotz Passwortschutz editiert werden | 2018-12-10 | 2019-01-04
| 2019-01-04 | Angabe zu Spannungsversorgung entfernt da derzeit nicht Hilfreich bei der Definition der Stromaufnahme |  | 2019-01-04 | 2019-01-04
| 2019-01-09 | AI43EX auf 70 °C umgestellt |  | 2019-01-09 | 2019-01-09
1.2 | 2019-01-09 | Freibage Version 1.2
1.3 d1 | 2020-06-09 | Ergänzung GEN-3G
1.3 | 2020-06-30 | Überführung in 1.3 ohne weiter Änderungen
1.3.1 | 2020-11-17 | In Introduction Predefined by Pressure … in… area geändert |  | 2020-11-17 | 2020-11-17
1.4.0 | 2022-08-18 | TI401EX aufgenommen |  | 2022-08-18 | 2022-08-18
| 2022-08-18 | Modulliste Spalte lfnr 1.4.0 ergänzt keine Referenzierung darauf im Programm notwendig |  | 2022-08-18 | 2022-08-18
1.4.1 | 2025-03-26 | Gleichzeitigkeitsfaktor für DO401EX hinzugefügt